Simple Guide
How to Add a New Sensor

Firmware and Admin Portal Steps

LoRa-Based Smart Building Management System

# 1. Main Idea

The system has one standard core and several small firmware builds. The core contains Wi-Fi provisioning, backend communication, LoRaWAN, saved configuration, and the main program flow.

When a new sensor is added, the developer does not rewrite the core. The developer adds a small sensor module, a payload encoder, and a registry entry. Then the administrator creates the sensor profile in the Admin Portal.

# 2. Parts That Stay Unchanged

Wi-Fi access point and provisioning page

Backend connection

Building, floor, and room selection

Device credentials and Preferences storage

LoRaWAN joining and uplink scheduling

TTN registration workflow

Main setup() and loop() structure

# 3. Quick Overview

| Who | What they do |
| --- | --- |
| Developer | Adds the new sensor driver and payload encoder to the firmware project. |
| Developer | Creates a small build that includes only the required sensor module. |
| Administrator | Adds the sensor and firmware module in the Admin Portal. |
| Administrator | Creates an Advanced Profile with payload, decoder, telemetry, and settings. |
| Administrator | Provisions the LILYGO using the new profile. |
| Tester | Checks Serial Monitor, TTN, backend, ThingsBoard, and Floor Live View. |

# Part A - Firmware Steps

## Step 1 - Study the New Sensor

Before coding, check the sensor datasheet and write down:

Power voltage

Communication type: I2C, SPI, UART, analog, pulse, or digital

Required pins or address

Measurement values and units

Required Arduino library

Valid measurement range

Warm-up time, timeout, or calibration requirements

## Step 2 - Connect the Sensor Safely

Connect the sensor to free LILYGO pins. Check that:

The voltage is correct

Ground is shared

The pins are not already used by LoRa, OLED, SPI, or boot functions

A voltage divider or level shifter is used when required

## Step 3 - Create the Sensor Driver

Add the new sensor files inside:

src/sensors/

Example file names:

NewSensorModule.h
NewSensorModule.cpp

The driver should contain:

begin() - starts the sensor

read() - reads the sensor values

Error and timeout handling

Clear Serial Monitor messages

## Step 4 - Create the Payload Encoder

Add the payload encoder inside:

src/payloads/

Example:

NewSensorV1Encoder.cpp

The encoder converts normal sensor values into LoRaWAN bytes. The byte order, scale, signed value, and payload length must be written clearly.

## Step 5 - Register the Sensor

Register the driver in:

src/framework/SensorRegistry.cpp

Register the payload encoder in:

src/framework/PayloadRegistry.cpp

Example module and encoder keys:

module_key: "new_sensor_i2c"
payload_encoder_key: "new_sensor_v1"

## Step 6 - Add the Build Option

Open:

BuildConfig.h

Add a build option for the new sensor. Example:

#define FW_PRESET_NEW_SENSOR 5

The new firmware build should include the standard core plus only the new sensor driver and its payload encoder. Do not compile every sensor library into every build.

## Step 7 - Compile and Test Locally

Before provisioning, verify:

The firmware compiles without errors

The flash percentage is acceptable

The sensor starts correctly

The values are realistic

The payload bytes are correct

Timeout and disconnected-sensor errors are handled

# Part B - Admin Portal Steps

## Step 8 - Add the Sensor to Sensor Catalog

Open:

/sensor-catalog-manager

Enter:

Sensor code

Manufacturer

Model

Use case

Protocol

Default bus

Default address, if used

Description

Enabled

This record describes the physical sensor. The sensor code must be unique.

## Step 9 - Add the Firmware Module

Open:

/firmware-module-manager

Enter:

Module key

Display name

Driver class

Protocol

Library name and version, if used

Supported board

Minimum firmware version

Source file

Enabled

The module key must be exactly the same as the key registered in the firmware.

## Step 10 - Create an Advanced Profile

Open:

/sensor-profile-editor/advanced

In General Information, enter:

Profile code

Profile name

Node type

Capabilities

Description

Status: Active

Enabled

## Step 11 - Configure Payload and Platform Mapping

Enter:

Payload encoder key

Payload version

LoRaWAN FPort

Uplink interval

ThingsBoard profile

Formatter type: JavaScript

Device configuration schema

The payload encoder key must match the encoder key in the firmware.

## Step 12 - Add the TTN Decoder

Write the JavaScript decoder so it reads the exact bytes created by the firmware. It should check the FPort, payload length, byte order, scale, and field names.

The returned telemetry keys must match the profile fields exactly.

## Step 13 - Add the Sensor Component

Select:

The sensor from Sensor Catalog

The firmware module

The role, normally primary

Required or optional

Sensor configuration such as pins, address, baud rate, or sample count

## Step 14 - Add Telemetry Fields

Create one field for every value sent by the sensor. Enter:

Field key

Label

Unit

Data type

Byte offset

Byte length

Scale

Signed or unsigned

Minimum and maximum value

Required

Floor visibility

Dashboard visibility

Display precision

The field positions and scales must match the firmware payload and the TTN decoder.

## Step 15 - Add Optional Alarm Rules

Add alarms only after normal telemetry is working. Choose the field, condition, threshold, severity, message, cooldown, and auto-resolve setting.

## Step 16 - Validate and Create the Profile

Click:

Validate Profile

Fix all errors, then click:

Create Profile

Check that the new profile appears in:

/provision-options

Create the profile on the real deployment backend, for example the Raspberry Pi. Profiles saved in a laptop database do not automatically appear in the Raspberry Pi database.

# Part C - Provisioning and Testing

## Step 17 - Upload the Correct Firmware Build

Upload the small firmware build that contains the standard core plus the new sensor module and encoder.

Open Serial Monitor at 115200 baud and confirm that the firmware starts correctly.

## Step 18 - Provision the LILYGO

Connect to:

Wi-Fi: LILYGO_Config
Password: 12345678

Open:

http://192.168.4.1

Select:

The new sensor profile

Building

Floor

Room

Device label

Then click Provision Device.

## Step 19 - Check the Automatic Workflow

The backend should automatically:

Create the local device record

Create or assign LoRaWAN credentials

Register the device in TTN

Install the JavaScript decoder

Create or map the ThingsBoard device

Save the building, floor, and room

Return the profile information to the LILYGO

## Step 20 - Test End to End

Check the full path:

Sensor -> LILYGO driver -> Payload encoder -> LoRaWAN gateway -> TTN decoder
-> Backend webhook -> ThingsBoard/database -> Floor Live View

Confirm:

Serial Monitor shows correct sensor values

TTN receives the expected payload length

TTN shows the correct decoded fields

The backend accepts the data

ThingsBoard receives the telemetry

The device and readings appear in Floor Live View

The device still works after restart

# 4. What to Change for Every New Sensor

| Firmware | Admin Portal |
| --- | --- |
| 1. Sensor driver 2. Payload encoder 3. Sensor registry entry 4. Payload registry entry 5. BuildConfig option | 1. Sensor Catalog record 2. Firmware Module record 3. Advanced Profile 4. TTN decoder 5. Telemetry fields 6. Optional alarm rules |

# 5. Very Simple Explanation

For a completely new sensor, the developer adds one small sensor driver and one payload encoder to the reusable firmware project. The standard Wi-Fi, backend, and LoRaWAN core stays unchanged. The administrator then adds the sensor, firmware module, payload decoder, telemetry fields, and settings through the Admin Portal. After that, the LILYGO is provisioned normally and the backend completes the TTN and dashboard setup automatically.

# 6. Final Checklist

☐ Sensor datasheet checked

☐ Safe wiring confirmed

☐ Driver created

☐ Payload encoder created

☐ Registry entries added

☐ Small build created

☐ Firmware compiled and tested

☐ Sensor Catalog record created

☐ Firmware Module record created

☐ Advanced Profile created

☐ TTN decoder added

☐ Telemetry fields added

☐ Profile validated

☐ LILYGO provisioned

☐ TTN and Floor Live View tested